{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":72,"n_cols":17,"rows_kept":72,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWAH-TZSLC2"]
[]
[]
[]
[]
["","","","","","EWAH710TZSLC2","EWAH770TZSLC2","EWAH880TZSLC2","EWAH940TZSLC2","EWAH990TZSLC2","EWAHH10TZSLC2","EWAHC11TZSLC2","EWAHC12TZSLC2","EWAHC13TZSLC2","EWAHC14TZSLC2","EWAHC15TZSLC2","EWAHC16TZSLC2"]
["Sound pressure level","Cooling","","Nom.","dBA","77"]
["Compressor","Type","","","","Inverter driven single screw compressor"]
["","Quantity","","","","2"]
["Weight","Operation weight","","","kg","7,313"]
["","Unit","","","kg","7,033"]
["Air heat exchanger","Type","","","","Microchannel"]
["EER","","","","","3.088","3.104","3.087","3.102","3.107","3.11","3.126","3.109","3.111","3.077","2.975","2.826"]
["Refrigerant","GWP","","","","7"]
["","Type","","","","R-1234(ze)"]
["","Circuits","","Quantity","","2"]
["","Charge","","","kg","120"]
["Cooling capacity","Nom.","","","kW","712.3"]
["Water heat exchanger","Water volume","","","l","280"]
["","Type","","","","Shell and tube"]
["Power input","Cooling","","Nom.","kW","230.7"]
["Sound power level","Cooling","","Nom.","dBA","98"]
["Dimensions","Unit","","Width","mm","2,280"]
["","","","Depth","mm","6,909"]
["","","","Height","mm","2,540"]
["Capacity control","Minimum capacity","","","%","12.5"]
["","Method","","","","Inverter controlled"]
["Fan","Air flow rate","","Nom.","l/s","71,438"]
["","Speed","","","rpm","900"]
["Compressor","Starting method","","","","VFD driven"]
["Power supply","Phase","","","","3~"]
["","Frequency","","","Hz","50"]
["","Voltage","","","V","400"]
["Notes","","","","","(1) - Standard Rating Conditions for Air to water chillers according to EN14511:2 Outdoor Heat exchanger inlet dry bulb temperature 35°; Indoor heat exchanger inlet water temperature 12°C, outlet water temperature 7°C. Fouling factor = 0","(1) - Standard Rating Conditions for Air to water chillers according to EN14511:2 Outdoor Heat exchanger inlet dry bulb temperature 35°; Indoor heat exchanger inlet water temperature 12°C, outlet water temperature 7°C. Fouling factor = 0","(1) - Standard Rating Conditions for Air to water chillers according to EN14511:2 Outdoor Heat exchanger inlet dry bulb temperature 35°; Indoor heat exchanger inlet water temperature 12°C, outlet water temperature 7°C. Fouling factor = 0","(1) - Standard Rating Conditions for Air to water chillers according to EN14511:2 Outdoor Heat exchanger inlet dry bulb temperature 35°; Indoor heat exchanger inlet water temperature 12°C, outlet water temperature 7°C. Fouling factor = 0","(1) - Standard Rating Conditions for Air to water chillers according to EN14511:2 Outdoor Heat exchanger inlet dry bulb temperature 35°; Indoor heat exchanger inlet water temperature 12°C, outlet water temperature 7°C. Fouling factor = 0","(1) - Standard Rating Conditions for Air to water chillers according to EN14511:2 Outdoor Heat exchanger inlet dry bulb temperature 35°; Indoor heat exchanger inlet water temperature 12°C, outlet water temperature 7°C. Fouling factor = 0","(1) - Standard Rating Conditions for Air to water chillers according to EN14511:2 Outdoor Heat exchanger inlet dry bulb temperature 35°; Indoor heat exchanger inlet water temperature 12°C, outlet water temperature 7°C. Fouling factor = 0","(1) - Standard Rating Conditions for Air to water chillers according to EN14511:2 Outdoor Heat exchanger inlet dry bulb temperature 35°; Indoor heat exchanger inlet water temperature 12°C, outlet water temperature 7°C. Fouling factor = 0","(1) - Standard Rating Conditions for Air to water chillers according to EN14511:2 Outdoor Heat exchanger inlet dry bulb temperature 35°; Indoor heat exchanger inlet water temperature 12°C, outlet water temperature 7°C. Fouling factor = 0","(1) - Standard Rating Conditions for Air to water chillers according to EN14511:2 Outdoor Heat exchanger inlet dry bulb temperature 35°; Indoor heat exchanger inlet water temperature 12°C, outlet water temperature 7°C. Fouling factor = 0","(1) - Standard Rating Conditions for Air to water chillers according to EN14511:2 Outdoor Heat exchanger inlet dry bulb temperature 35°; Indoor heat exchanger inlet water temperature 12°C, outlet water temperature 7°C. Fouling factor = 0","(1) - Standard Rating Conditions for Air to water chillers according to EN14511:2 Outdoor Heat exchanger inlet dry bulb temperature 35°; Indoor heat exchanger inlet water temperature 12°C, outlet water temperature 7°C. Fouling factor = 0"]
["","","","","","(2) - Voltage unbalance between phases must be within ± 3%.","(2) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(2) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(2) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(2) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(2) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(2) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(2) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(2) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(2) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(2) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(2) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current"]
["","","","","","(3) - Maximum running current is based on max compressor absorbed current in its envelope and max fans absorbed current","(3) - Based on minimum allowed voltage à Max. current for wire sizing = Max. Running current x 1,1","(3) - Based on minimum allowed voltage à Max. current for wire sizing = Max. Running current x 1,1","(3) - Based on minimum allowed voltage à Max. current for wire sizing = Max. Running current x 1,1","(3) - Based on minimum allowed voltage à Max. current for wire sizing = Max. Running current x 1,1","(3) - Based on minimum allowed voltage à Max. current for wire sizing = Max. Running current x 1,1","(3) - Based on minimum allowed voltage à Max. current for wire sizing = Max. Running current x 1,1","(3) - Based on minimum allowed voltage à Max. current for wire sizing = Max. Running current x 1,1","(3) - Based on minimum allowed voltage à Max. current for wire sizing = Max. Running current x 1,1","(3) - Based on minimum allowed voltage à Max. current for wire sizing = Max. Running current x 1,1","(3) - Based on minimum allowed voltage à Max. current for wire sizing = Max. Running current x 1,1","(3) - Based on minimum allowed voltage à Max. current for wire sizing = Max. Running current x 1,1"]
["","","","","","(4) - Based on minimum allowed voltage à Max. current for wire sizing = Max. Running current x 1,1","(4) - In case of inverter driven compressor, the starting current is zero","(4) - In case of inverter driven compressor, the starting current is zero","(4) - In case of inverter driven compressor, the starting current is zero","(4) - In case of inverter driven compressor, the starting current is zero","(4) - In case of inverter driven compressor, the starting current is zero","(4) - In case of inverter driven compressor, the starting current is zero","(4) - In case of inverter driven compressor, the starting current is zero","(4) - In case of inverter driven compressor, the starting current is zero","(4) - In case of inverter driven compressor, the starting current is zero","(4) - In case of inverter driven compressor, the starting current is zero","(4) - In case of inverter driven compressor, the starting current is zero"]
["","","","","","(5) - In case of inverter driven compressor, the starting current is zero","(5) - It may change in case of unit with options or customized unit. Refer to dedicated unit’s wiring diagram.","(5) - It may change in case of unit with options or customized unit. Refer to dedicated unit’s wiring diagram.","(5) - It may change in case of unit with options or customized unit. Refer to dedicated unit’s wiring diagram.","(5) - It may change in case of unit with options or customized unit. Refer to dedicated unit’s wiring diagram.","(5) - It may change in case of unit with options or customized unit. Refer to dedicated unit’s wiring diagram.","(5) - It may change in case of unit with options or customized unit. Refer to dedicated unit’s wiring diagram.","(5) - It may change in case of unit with options or customized unit. Refer to dedicated unit’s wiring diagram.","(5) - It may change in case of unit with options or customized unit. Refer to dedicated unit’s wiring diagram.","(5) - It may change in case of unit with options or customized unit. Refer to dedicated unit’s wiring diagram.","(5) - It may change in case of unit with options or customized unit. Refer to dedicated unit’s wiring diagram.","(5) - It may change in case of unit with options or customized unit. Refer to dedicated unit’s wiring diagram."]
["","","","","","(6) - It may change in case of unit with options or customized unit. Refer to dedicated unit’s wiring diagram."]
["","","","","","(7) - The data are referred to the unit without additional options."]
["","","","","","(8) - All data are subject to change without notice. For updated information on project base refer to unit specific wiring diagram and unit’s nameplate data."]
["Cooling capacity","Nom.","","","kW","","765.6","879.4","942.8","990.5","1056","1117","1231","1302","1432","1519","1603"]
["Capacity control","Method","","","","","Inverter controlled","Inverter controlled","Inverter controlled","Inverter controlled","Inverter controlled","Inverter controlled","Inverter controlled","Inverter controlled","Inverter controlled","Inverter controlled","Inverter controlled"]
["","Minimum capacity","","","%","","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5","12.5"]
["Power input","Cooling","","Nom.","kW","","246.6","284.9","303.9","318.9","339.4","357.4","396","418.4","465.3","510.4","567.4"]
["IPLV","","","","","","4.85","4.8","4.74","4.78","4.71","4.73","4.63","5.17","5.08","5.07","4.98"]
["SEER","","","","","","4.652","4.629","4.618","4.646","4.61","4.631","4.557","4.922","4.883","4.844","4.798"]
["Dimensions","Unit","","Depth","mm","","6909","7809","8709","9602","10510","11402","12302","11402","12302","13202","14102"]
["","","","Height","mm","","2540","2540","2540","2540","2540","2540","2540","2540","2540","2540","2540"]
["","","","Width","mm","","2280","2280","2280","2280","2280","2280","2280","2280","2280","2280","2280"]
["Weight","Operation weight","","","kg","","7313","8152","8585","9483","9871","11116","11518","11727","12145","12575","13048"]
["","Unit","","","kg","","7033","7660","8093","8900","9288","10073","10475","10716","11134","11564","12037"]
["Casing","Colour","","","","","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white","Ivory white"]
["","Material","","","","","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet","Galvanized and painted steel sheet"]
["Fan","Quantity","","","","","14","16","18","20","22","24","26","24","26","28","30"]
["","Type","","","","","Direct propeller, on/off fans","Direct propeller, on/off fans","Direct propeller, on/off fans","Direct propeller, on/off fans","Direct propeller, on/off fans","Direct propeller, on/off fans","Direct propeller, on/off fans","Direct propeller, on/off fans","Direct propeller, on/off fans","Direct propeller, on/off fans","Direct propeller, on/off fans"]
["Compressor","Quantity","","","","","2","2","2","2","2","2","2","2","2","2","2"]
["","Type","","","","","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor","Inverter driven single screw compressor"]
["","Starting method","","","","","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven","VFD driven"]
["Sound power level","Cooling","","Nom.","dBA","","98","99","100","101","101","102","103","102","102","103","104"]
["Sound pressure level","Cooling","","Nom.","dBA","","77","77","78","78","79","79","80","79","79","80","80"]
["Refrigerant","GWP","","","","","7","7","7","7","7","7","7","7","7","7","7"]
["","Charge","","","kg","","120","130","141","150","175","200","220","200","220","250","270"]
["","Circuits","","Quantity","","","2","2","2","2","2","2","2","2","2","2","2"]
["Power supply","Frequency","","","Hz","","50","50","50","50","50","50","50","50","50","50","50"]
["","Voltage range","","Min.","%","","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","","","Max.","%","","10","10","10","10","10","10","10","10","10","10","10"]
["Unit","Starting current","","Max","A","","0 (5)","0 (5)","0 (5)","0 (5)","0 (5)","0 (5)","0 (5)","0 (5)","0 (5)","0 (5)","0 (5)"]
["","Running current","Cooling","Nom.","A","","433.3 (1)","493.5 (1)","521.5 (1)","549.9 (1)","579.6 (1)","612.7 (1)","668.8 (1)","718.8 (1)","780.9 (1)","848.9 (1)","934.8 (1)"]
["","","","Max","A","","640.0 (3)","717.0 (3)","763.0 (3)","811.0 (3)","869.0 (3)","924.0 (3)","1032.0 (3)","1029.0 (3)","1119.0 (3)","1198.0 (3)","1226.0 (3)"]
["","Max unit current for wires sizing","","","A","","704.0 (4)","789.0 (4)","839.0 (4)","892.0 (4)","956.0 (4)","1016.0 (4)","1135.0 (4)","1132.0 (4)","1231.0 (4)","1318.0 (4)","1349.0 (4)"]
["Piping connections","Evaporator water inlet/outlet (OD)","","","","","","219.1mm","219.1mm","219.1mm","219.1mm","273mm","273mm","273mm","273mm","273mm","273mm"]