{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":138,"n_cols":29,"rows_kept":138,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RYYQ-T"]
[]
[]
[]
[]
["","","","","","RYYQ8T7Y1B","RYYQ18T7Y1B","RYYQ20T7Y1B","RYYQ30T7Y1B","RYYQ34T7Y1B","RYYQ40T7Y1B","RYYQ50T7Y1B","RYYQ52T7Y1B","RYYQ54T7Y1B","RYYQ10T7Y1B (Archived)","RYYQ12T7Y1B (Archived)","RYYQ14T7Y1B (Archived)","RYYQ16T7Y1B (Archived)","RYYQ22T7Y1B (Archived)","RYYQ24T7Y1B (Archived)","RYYQ26T7Y1B (Archived)","RYYQ28T7Y1B (Archived)","RYYQ32T7Y1B (Archived)","RYYQ36T7Y1B (Archived)","RYYQ38T7Y1B (Archived)","RYYQ42T7Y1B (Archived)","RYYQ44T7Y1B (Archived)","RYYQ46T7Y1B (Archived)","RYYQ48T7Y1B (Archived)"]
["Sound pressure level","Cooling","","Nom.","dBA","","65.0 (5)","66.0 (5)","66.5 (5)","67.5 (5)","67.0 (5)","69.1 (5)","69.5 (5)","69.8 (5)","58.0 (5)","61.0 (5)","61.0 (5)","64.0 (5)","62.8 (5)","65.0 (5)","64.0 (5)","65.8 (5)","67.0 (5)","68.1 (5)","67.2 (5)","67.5 (5)","68.0 (5)","68.0 (5)","68.8 (5)"]
["Capacity range","HP","","","","8","18","20","30","34","40","50","52","54","10","12","14","16","22","24","26","28","32","36","38","42","44","46","48"]
["Operation range","Cooling","","Max.","°CDB","","43.0","43.0","","","","","","","43.0","43.0","43.0","43.0"]
["","","","Min.","°CDB","","-5.0","-5.0","","","","","","","-5.0","-5.0","-5.0","-5.0"]
["","Heating","","Min.","°CWB","","-20.0","-20.0","","","","","","","-20.0","-20.0","-20.0","-20.0"]
["Maximum number of connectable indoor units","","","","","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)","64 (3)"]
["Space cooling","B Condition (30°C - 27/19)","","Pdc","kW","","37.1","38.3","61.8","70.3","82.4","103.4","107.4","111.4","20.6","24.7","29.5","33.2","45.3","49.7","54.2","57.8","66.3","71.5","75.5","86.9","91.0","95.8","99.5"]
["","D Condition (20°C - 27/19)","","Pdc","kW","","10.6","10.9","17.7","20.1","23.6","29.6","30.7","31.8","6.9","7.1","8.4","9.5","13.0","14.3","15.5","16.6","18.9","20.4","21.6","24.8","26.0","27.4","28.4"]
["","A Condition (35°C - 27/19)","","Pdc","kW","","50.4","52.0","83.9","95.4","111.9","140.4","145.8","151.2","28.0","33.5","40.0","45.0","61.5","67.4","73.5","78.5","90.0","97.0","102.4","118.0","123.5","130.0","135.0"]
["","C Condition (25°C - 27/19)","","Pdc","kW","","23.9","24.6","39.7","45.2","53.0","66.5","69.1","71.6","13.3","15.9","18.9","21.3","29.1","31.9","34.8","37.2","42.6","46.0","48.5","55.9","58.5","61.6","63.9"]
["Compressor","Type","","","","","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","","","","","","","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor","Hermetically sealed scroll compressor"]
["Weight","Unit","","","kg","","391","391","","","","","","","252","252","356","356"]
["Refrigerant","Charge","","","TCO2Eq","","24.4","24.6","","","","","","","12.5","13.2","21.5","21.7"]
["","GWP","","","","","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5","2,087.5"]
["","Charge","","","kg","","11.7","11.8","","","","","","","6.0","6.3","10.3","10.4"]
["","Type","","","","","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A","R-410A"]
["System","Outdoor unit module 2","","","","","","","RYMQ18T","RYMQ18T","RYMQ12T","RYMQ16T","RYMQ18T","RYMQ18T","","","","","RYMQ12T","RYMQ16T","RYMQ14T","RYMQ16T","RYMQ16T","RYMQ20T","RYMQ10T","RYMQ16T","RYMQ16T","RYMQ16T","RYMQ16T"]
["","Outdoor unit module 3","","","","","","","","","RYMQ18T","RYMQ18T","RYMQ18T","RYMQ18T","","","","","","","","","","","RYMQ20T","RYMQ16T","RYMQ16T","RYMQ16T","RYMQ16T"]
["","Outdoor unit module 1","","","","","","","RYMQ12T","RYMQ16T","RYMQ10T","RYMQ16T","RYMQ16T","RYMQ18T","","","","","RYMQ10T","RYMQ8T","RYMQ12T","RYMQ12T","RYMQ16T","RYMQ16T","RYMQ8T","RYMQ10T","RYMQ12T","RYMQ14T","RYMQ16T"]
["Indoor index connection","Min.","","","","","225.0","250.0","375.0","425.0","500.0","625.0","650.0","675.0","125.0","150.0","175.0","200.0","275.0","300.0","325.0","350.0","400.0","450.0","475.0","525.0","550.0","575.0","600.0"]
["","Max.","","","","","585.0","650.0","975.0","1,105.0","1,300.0","1,625.0","1,690.0","1,755.0","325.0","390.0","455.0","520.0","715.0","780.0","845.0","910.0","1,040.0","1,170.0","1,235.0","1,365.0","1,430.0","1,495.0","1,560.0"]
["Space heating (Average climate)","TOL","","Pdh (declared heating cap)","kW","","27.9","31.0","44.4","51.1","58.9","74.3","79.0","83.7","16.0","18.4","20.6","23.2","34.4","36.9","37.1","39.7","46.4","54.2","58.2","60.9","62.9","67.0","69.6"]
["","","","Tol (temperature operating limit)","°C","","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","D Condition (12°C)","","Pdh (declared heating cap)","kW","","5.8","5.9","6.8","7.9","9.1","11.4","12.1","12.9","6.1","6.2","4.0","4.1","6.2","6.6","6.2","6.2","8.3","8.3","9.0","10.3","10.3","12.3","12.4"]
["","B Condition (2°C)","","Pdh (declared heating cap)","kW","","15.0","16.7","23.9","27.5","31.7","40.0","42.5","45.1","8.6","9.9","11.1","12.5","18.5","19.8","20.0","21.4","25.0","29.2","31.3","32.8","33.8","36.1","37.4"]
["","C Condition (7°C)","","Pdh (declared heating cap)","kW","","9.7","10.7","15.4","17.7","20.4","25.7","27.3","29.0","6.5","6.4","7.1","8.0","12.9","12.8","12.8","13.7","16.0","18.8","20.1","21.1","21.9","23.2","24.1"]
["","A Condition (-7°C)","","Pdh (declared heating cap)","kW","","24.7","27.4","39.3","45.2","52.1","65.7","69.9","74.0","14.2","16.3","18.2","20.5","30.4","32.6","32.8","35.1","41.0","47.9","51.5","53.8","55.6","59.2","61.5"]
["","TBivalent","","Pdh (declared heating cap)","kW","","27.9","31.0","44.4","51.1","58.9","74.3","79.0","83.7","16.0","18.4","20.6","23.2","34.4","36.9","37.1","39.7","46.4","54.2","58.2","60.9","62.9","67.0","69.6"]
["","","","Tbiv (bivalent temperature)","°C","","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["Piping connections","Liquid","","OD","mm","","15.9","15.9","19.1","19.1","19.1","19.1","19.1","19.1","9.52","12.7","12.7","12.7","15.9","15.9","19.1","19.1","19.1","19.1","19.1","19.1","19.1","19.1","19.1"]
["","","","Type","","","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection"]
["","Total piping length","System","Actual","m","","1,000 (6)","1,000 (6)","1,000 (6)","1,000 (6)","1,000 (6)","1,000 (6)","1,000 (6)","1,000 (6)","1,000 (6)","1,000 (6)","1,000 (6)","1,000 (6)","1,000 (6)","1,000 (6)","1,000 (6)","1,000 (6)","1,000 (6)","1,000 (6)","1,000 (6)","1,000 (6)","1,000 (6)","1,000 (6)","1,000 (6)"]
["","Gas","","OD","mm","","28.6","28.6","34.9","34.9","41.3","41.3","41.3","41.3","22.2","28.6","28.6","28.6","28.6","34.9","34.9","34.9","34.9","41.3","41.3","41.3","41.3","41.3","41.3"]
["","","","Type","","","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection","Braze connection"]
["Dimensions","Unit","","Width","mm","","1,240","1,240","","","","","","","930","930","1,240","1,240"]
["","","","Depth","mm","","765","765","","","","","","","765","765","765","765"]
["","","","Height","mm","","1,685","1,685","","","","","","","1,685","1,685","1,685","1,685"]
["Continuous heating","","","","","","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes","Yes"]
["Fan","External static pressure","","Max.","Pa","","78","78","","","","","","","78","78","78","78"]
["Power supply","Phase","","","","","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~","3N~"]
["","Name","","","","","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1","Y1"]
["","Frequency","","","Hz","","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50","50"]
["","Voltage","","","V","","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415","380-415"]
["Piping connections","Heat insulation","","","","Both liquid and gas pipes"]
["Cooling capacity","Nom.","","35°CDB","kW","22.4 (1)"]
["","","","Eurovent","kW","22.4 (28)"]
["Heating capacity","Nom.","","6°CWB","kW","22.4 (2)"]
["","","","Eurovent","kW","22.40 (29)"]
["EER at nom. capacity","35°CDB","","","KW/KW","4.30 (1)"]
["COP at nom. capacity","6°CWB","","","KW/KW","4.72 (2)"]
["","Eurovent","","","KW/KW","5.01 (29)"]
["Indoor index connection","Min.","","","","100"]
["","Nom.","","","","200"]
["","Max.","","","","260"]
["Dimensions","Unit","","Height","mm","1685"]
["","","","Width","mm","930"]
["","","","Depth","mm","765"]
["Weight","Unit","","","kg","243"]
["Fan","Air flow rate","Cooling","Nom.","m³/min","162"]
["","External static pressure","","Max.","Pa","78"]
["Compressor","Type","","","","Hermetically sealed scroll compressor"]
["Operation range","Cooling","","Min.","°CDB","-5"]
["","","","Max.","°CDB","43"]
["","Heating","","Min.","°CWB","-20"]
["","","","Max.","°CWB","15.5"]
["Sound power level","Cooling","","Nom.","dBA","78"]
["Sound pressure level","Cooling","","Nom.","dBA","58"]
["Refrigerant","Type","","","","R-410A"]
["","GWP","","","","2087.5"]
["","Charge","","","tCO2Eq","12.3"]
["","Charge","","","kg","5.9"]
["Piping connections","Liquid","","Type","","Braze connection"]
["","","","OD","mm","9.52"]
["","Gas","","Type","","Braze connection"]
["","","","OD","mm","19.1"]
["","Total piping length","System","Actual","m","1000 (7)"]
["","Level difference","OU - IU","Outdoor unit in highest position","m","90 (7)"]
["","","","Indoor unit in highest position","m","90 (7)"]
["","","IU - IU","Max.","m","30 (7)"]
["Standard Accessories","Connection pipes","","","","Connection pipes","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1"]
["","Installation and operation manual","","","","Installation and operation manual"]
["Power supply","Name","","","","Y1"]
["","Phase","","","","3N~"]
["","Frequency","","","Hz","50"]
["","Voltage","","","V","380-415"]
["Notes","","","","","(1) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m. Data for standard efficiency series","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m","(1) - Cooling: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB; equivalent piping length: 7.5m; level difference: 0m"]
["","","","","","(2) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m. Data for standard efficiency series","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m","(2) - Heating: indoor temp. 20°CDB; outdoor temp. 7°CDB, 6°CWB; equivalent refrigerant piping: 7.5m; level difference: 0m"]
["","","","","","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)","(3) - Actual number of connectable indoor units depends on the indoor unit type (VRV indoor, Hydrobox, RA indoor, etc.) and the connection ratio restriction for the system (50% <= CR <= 130%)"]
["","","","","","(4) - For more details on operation range see TW drawing","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates.","(4) - Sound power level is an absolute value that a sound source generates."]
["","","","","","(5) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(5) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings."]
["","","","","","(6) - Maximum allowable voltage range variation between phases is 2%.","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual","(6) - Refer to refrigerant pipe selection or installation manual"]
["","","","","","(7) - Refer to refrigerant pipe selection or installation manual","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(7) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB"]
["","","","","","(8) - For more details on standard accessories refer to Installation/operation manual","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(8) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current."]
["","","","","","(9) - RLA is based on following conditions: indoor temp. 27°CDB, 19°CWB; outdoor temp. 35°CDB","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value","(9) - In accordance with EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply wih Ssc  ≥ minimum Ssc value"]
["","","","","","(10) - MSC means the maximum current during start up of the compressor. This unit uses only inverter compressors. Starting current is always ≤ max. running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current.","(10) - MCA must be used to select the correct field wiring size. The MCA can be regarded as the maximum running current."]
["","","","","","(11) - Select wire size based on the value of MCA. The MCA can be regarded as the maximum running current.","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(11) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker)."]
["","","","","","(12) - MFA is used to select the circuit breaker and the ground fault circuit interrupter (earth leakage circuit breaker).","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set.","(12) - TOCA means the total value of each OC set."]
["","","","","","(13) - TOCA means the total value of each OC set.","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan","(13) - FLA means the nominal running current of the fan"]
["","","","","","(14) - FLA means the nominal running current of the fan","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%.","(14) - Maximum allowable voltage range variation between phases is 2%."]
["","","","","","(15) - In accordance with EN/IEC 61000-3-11, respectively EN/IEC 61000-3-12, it may be necessary to consult the distribution network operator to ensure that the equipment is connected only to a supply with Zsys ≤ Zmax, respectively Ssc ≥ minimum Ssc value.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits.","(15) - Voltage range: units are suitable for use on electrical systems where voltage supplied to unit terminal is not below or above listed range limits."]
["","","","","","(16) - European/International Technical Standard setting the limits for voltage changes, voltage fluctuations and flicker in public low-voltage supply systems for equipment with rated current ≤ 75A.","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )","(16) - The AUTOMATIC ESEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation funcitonality ( variable refrigerant temperature )"]
["","","","","","(17) - European/International Technical Standard setting the limits for harmonic currents produced by equipment connected to public low-voltage systems with input current >16A and <= 75Aper phase","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality","(17) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality"]
["","","","","","(18) - Short-circuit power","(18) - Sound values are measured in a semi-anechoic room.","(18) - Sound values are measured in a semi-anechoic room.","(18) - Sound values are measured in a semi-anechoic room.","(18) - Sound values are measured in a semi-anechoic room.","(18) - Sound values are measured in a semi-anechoic room.","(18) - Sound values are measured in a semi-anechoic room.","(18) - Sound values are measured in a semi-anechoic room.","(18) - Sound values are measured in a semi-anechoic room.","(18) - Sound values are measured in a semi-anechoic room.","(18) - Sound values are measured in a semi-anechoic room.","(18) - Sound values are measured in a semi-anechoic room.","(18) - Sound values are measured in a semi-anechoic room.","(18) - Sound values are measured in a semi-anechoic room.","(18) - Sound values are measured in a semi-anechoic room.","(18) - Sound values are measured in a semi-anechoic room.","(18) - Sound values are measured in a semi-anechoic room.","(18) - Sound values are measured in a semi-anechoic room.","(18) - Sound values are measured in a semi-anechoic room.","(18) - Sound values are measured in a semi-anechoic room.","(18) - Sound values are measured in a semi-anechoic room.","(18) - Sound values are measured in a semi-anechoic room.","(18) - Sound values are measured in a semi-anechoic room.","(18) - Sound values are measured in a semi-anechoic room."]
["","","","","","(19) - system impedance","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA","(19) - Soundpressure system [dBA] = 10*log[10^(A/10)+10^(B/10)+10^(C/10)] , with Unit A = A dBA, Unit B = B dBA, Unit C = C dBA"]
["","","","","","(20) - Multi combination (22~54HP) data is corresponding with the standard multi combination as mentioned on 3D079534","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase","(20) - EN/IEC 61000-3-12: European/international technical standard setting the limits for harmonic currents produced by equipment connected to public low-voltage system with input current > 16A and ≤ 75A per phase"]
["","","","","","(21) - Sound power level is an absolute value that a sound source generates.","(21) - Ssc: Short-circuit power","(21) - Ssc: Short-circuit power","(21) - Ssc: Short-circuit power","(21) - Ssc: Short-circuit power","(21) - Ssc: Short-circuit power","(21) - Ssc: Short-circuit power","(21) - Ssc: Short-circuit power","(21) - Ssc: Short-circuit power","(21) - Ssc: Short-circuit power","(21) - Ssc: Short-circuit power","(21) - Ssc: Short-circuit power","(21) - Ssc: Short-circuit power","(21) - Ssc: Short-circuit power","(21) - Ssc: Short-circuit power","(21) - Ssc: Short-circuit power","(21) - Ssc: Short-circuit power","(21) - Ssc: Short-circuit power","(21) - Ssc: Short-circuit power","(21) - Ssc: Short-circuit power","(21) - Ssc: Short-circuit power","(21) - Ssc: Short-circuit power","(21) - Ssc: Short-circuit power","(21) - Ssc: Short-circuit power"]
["","","","","","(22) - Sound pressure level is a relative value, depending on the distance and acoustic environment. For more details, please refer to the sound level drawings.","(22) - For detailed contents of standard accessories, see installation/operation manual","(22) - For detailed contents of standard accessories, see installation/operation manual","(22) - For detailed contents of standard accessories, see installation/operation manual","(22) - For detailed contents of standard accessories, see installation/operation manual","(22) - For detailed contents of standard accessories, see installation/operation manual","(22) - For detailed contents of standard accessories, see installation/operation manual","(22) - For detailed contents of standard accessories, see installation/operation manual","(22) - For detailed contents of standard accessories, see installation/operation manual","(22) - For detailed contents of standard accessories, see installation/operation manual","(22) - For detailed contents of standard accessories, see installation/operation manual","(22) - For detailed contents of standard accessories, see installation/operation manual","(22) - For detailed contents of standard accessories, see installation/operation manual","(22) - For detailed contents of standard accessories, see installation/operation manual","(22) - For detailed contents of standard accessories, see installation/operation manual","(22) - For detailed contents of standard accessories, see installation/operation manual","(22) - For detailed contents of standard accessories, see installation/operation manual","(22) - For detailed contents of standard accessories, see installation/operation manual","(22) - For detailed contents of standard accessories, see installation/operation manual","(22) - For detailed contents of standard accessories, see installation/operation manual","(22) - For detailed contents of standard accessories, see installation/operation manual","(22) - For detailed contents of standard accessories, see installation/operation manual","(22) - For detailed contents of standard accessories, see installation/operation manual","(22) - For detailed contents of standard accessories, see installation/operation manual"]
["","","","","","(23) - Sound values are measured in a semi-anechoic room.","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination","(23) - Multi combination (22~54HP) data is corresponding with the standard multi combination"]
["","","","","","(24) - The STANDARD ESEER value corresponds with normal VRV4 Heat Pump operation, not taking into account advanced energy saving operation functionality"]
["","","","","","(25) - The AUTOMATIC SEER value corresponds with normal VRV4 Heat Pump operation, taking into account advanced energy saving operation functionality ( variable refrigerant temperature control operation)"]
["","","","","","(26) - Nominal cooling capacities are based on: indoor temperature: 27°CDB, 19°CWB, outdoor temperature: 35°CDB, equivalent refrigerant piping: 5m, level difference: 0m. Data for high efficiency series, Eurovent certified"]
["","","","","","(27) - Nominal heating capacities are based on: indoor temperature: 20°CDB, outdoor temperature: 7°CDB, 6°CWB, equivalent refrigerant piping: 5m, level difference: 0m. Data for high efficiency series, Eurovent certified"]
["","","","","","(28) - Contains fluorinated greenhouse gases"]
["Standard Accessories","Installation manual","","","","","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1"]
["","Operation manual","","","","","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1","1"]
["Operation range","Heating","","Max.","°CWB","","15.5","15.5","","","","","","","15.5","15.5","15.5","15.5"]
["Space cooling","B Condition (30°C - 27/19)","","EERd","","","3.7","3.6","3.9","3.8","4.0","3.9","3.8","3.7","4.4","4.2","4.3","4.0","4.3","4.0","4.2","4.0","4.0","3.8","3.9","4.1","4.0","4.0","4.0"]
["","D Condition (20°C - 27/19)","","EERd","","","11.8","11.7","10.3","10.9","9.8","10.6","11.2","11.8","8.9","8.7","9.5","10.0","7.6","9.5","9.1","9.4","10.0","10.9","10.0","9.5","9.6","9.9","10.0"]
["","A Condition (35°C - 27/19)","","EERd","","","2.1","1.9","2.2","2.1","2.3","2.1","2.1","2.1","2.7","2.6","2.6","2.1","2.6","2.2","2.6","2.3","2.1","2.0","2.2","2.3","2.2","2.3","2.1"]
["","C Condition (25°C - 27/19)","","EERd","","","6.7","6.6","6.7","6.8","6.7","6.8","6.8","6.7","6.7","6.6","7.0","6.8","6.6","6.7","6.8","6.7","6.8","6.7","6.6","6.8","6.8","6.9","6.8"]
["SCOP","","","","","","3.6","3.7","3.5","3.6","3.7","3.6","3.6","3.6","3.8","3.8","3.5","3.5","3.8","3.7","3.7","3.6","3.5","3.7","3.7","3.7","3.7","3.5","3.5"]
["Cooling capacity","Prated,c","","","kW","","50.4 (1)","52.0 (1)","83.9 (1)","95.4 (1)","111.9 (1)","140.4 (1)","145.8 (1)","151.2 (1)","28.0 (1)","33.5 (1)","40.0 (1)","45.0 (1)","61.5 (1)","67.4 (1)","73.5 (1)","78.5 (1)","90.0 (1)","97.0 (1)","102.4 (1)","118.0 (1)","123.5 (1)","130.0 (1)","135.0 (1)"]
["Recommended combination","","","","","","3 x FXMQ50P7VEB + 5 x FXMQ63P7VEB","2 x FXMQ50P7VEB + 6 x FXMQ63P7VEB","9 x FXMQ50P7VEB + 5 x FXMQ63P7VEB","3 x FXMQ50P7VEB + 9 x FXMQ63P7VEB + 2 x FXMQ80P7VEB","9 x FXMQ50P7VEB + 9 x FXMQ63P7VEB","3 x FXMQ50P7VEB + 13 x FXMQ63P7VEB + 4 x FXMQ80P7VEB","6 x FXMQ50P7VEB + 14 x FXMQ63P7VEB + 2 x FXMQ80P7VEB","9 x FXMQ50P7VEB + 15 x FXMQ63P7VEB","4 x FXMQ63P7VEB","6 x FXMQ50P7VEB","1 x FXMQ50P7VEB + 5 x FXMQ63P7VEB","4 x FXMQ63P7VEB + 2 x FXMQ80P7VEB","6 x FXMQ50P7VEB + 4 x FXMQ63P7VEB","4 x FXMQ50P7VEB + 4 x FXMQ63P7VEB + 2 x FXMQ80P7VEB","7 x FXMQ50P7VEB + 5 x FXMQ63P7VEB","6 x FXMQ50P7VEB + 4 x FXMQ63P7VEB + 2 x FXMQ80P7VEB","8 x FXMQ63P7VEB + 4 x FXMQ80P7VEB","2 x FXMQ50P7VEB + 10 x FXMQ63P7VEB + 2 x FXMQ80P7VEB","6 x FXMQ50P7VEB + 10 x FXMQ63P7VEB","12 x FXMQ63P7VEB + 4 x FXMQ80P7VEB","6 x FXMQ50P7VEB + 8 x FXMQ63P7VEB + 4 x FXMQ80P7VEB","1 x FXMQ50P7VEB + 13 x FXMQ63P7VEB + 4 x FXMQ80P7VEB","12 x FXMQ63P7VEB + 6 x FXMQ80P7VEB"]
["Space heating (Average climate)","TOL","","COPd (declared COP)","","","1.8","2.0","1.9","1.8","2.0","1.8","1.8","1.8","2.0","2.1","1.9","1.7","2.1","1.8","2.0","1.9","1.7","1.9","2.1","1.8","1.8","1.8","1.7"]
["","D Condition (12°C)","","COPd (declared COP)","","","7.0","7.0","7.0","6.9","6.7","5.6","7.0","7.1","7.7","8.0","3.9","4.1","8.0","8.4","8.0","8.0","4.1","6.9","6.7","5.7","5.8","4.0","4.1"]
["","B Condition (2°C)","","COPd (declared COP)","","","3.5","3.6","3.4","3.4","3.3","3.4","3.4","3.5","3.2","3.2","3.3","3.3","3.2","3.2","3.3","3.3","3.3","3.5","3.4","3.3","3.3","3.3","3.3"]
["","C Condition (7°C)","","COPd (declared COP)","","","4.4","4.5","4.3","4.9","5.5","5.1","4.7","4.4","6.7","7.0","5.6","5.6","6.9","6.0","5.5","5.4","5.6","4.9","5.4","6.0","6.0","5.6","5.6"]
["","A Condition (-7°C)","","COPd (declared COP)","","","2.5","2.5","2.4","2.3","2.4","2.3","2.4","2.5","2.3","2.3","2.2","2.2","2.3","2.2","2.2","2.2","2.2","2.3","2.4","2.2","2.2","2.2","2.2"]
["","TBivalent","","COPd (declared COP)","","","1.8","2.0","1.9","1.8","2.0","1.8","1.8","1.8","2.0","2.1","1.9","1.7","2.1","1.8","2.0","1.9","1.7","1.9","2.1","1.8","1.8","1.8","1.7"]
["SEER","","","","","","5.5","5.3","5.5","5.5","5.5","5.5","5.5","5.5","5.6","5.5","5.7","5.5","5.4","5.5","5.6","5.5","5.5","5.4","5.4","5.5","5.5","5.6","5.5"]
["Sound power level","Cooling","","Nom.","dBA","","86.0 (4)","88.0 (4)","87.2 (4)","89.0 (4)","87.8 (4)","90.8 (4)","90.8 (4)","90.8 (4)","79.0 (4)","81.0 (4)","81.0 (4)","86.0 (4)","83.1 (4)","86.6 (4)","84.0 (4)","87.2 (4)","89.0 (4)","90.1 (4)","88.9 (4)","89.4 (4)","89.6 (4)","89.6 (4)","90.8 (4)"]
["Heating capacity","Prated,h","","","kW","","27.9","31.0","44.4","51.1","58.9","74.3","79.0","83.7","16.0","18.4","20.6","23.2","34.4","36.9","37.1","39.7","46.4","54.2","58.2","60.9","62.9","67.0","69.6"]